## STAKSHT
REV. NO. | DATE | DESCRIPTION | [6 empty] | BY | [12 empty] | DESIGNER |  | DATE
0 | 2018-01-26 | ISSUED FOR CONSTRUCTION. | [6 empty] | CWV | GRAY STASSEL ENGINEERING, INC. | [11 empty] | CWV |  | 2018-01-26 |  | TWIN HILLS RURAL POWER
[10 empty] | 1309 EAST KLATT ROAD, SUITE C | [11 empty] | CHECKER |  | DATE |  | SYSTEM UPGRADE
[10 empty] | ANCHORAGE, ALASKA 99511 | [11 empty] | CWV |  | 2018-01-26 |  | TWIN HILLS DISTRIBUTION
[10 empty] | (907) 349-0100 | [11 empty] | DIST. ENG. |  | DATE |  |  |  |  | Total ACSR = | 25798 | FEET
[22 empty] | CWV |  | 2018-01-26 |  |  |  |  | Total #4/0 Triplex = | 2880 | FEET
[29 empty] | Estimated #2 Triplex = | 2550 | FEET
[18 empty] | SECONDARY CONDUCTOR |  |  |  |  | MISCELLANEOUS
|  | LINE | CONDUCTOR |  |  |  |  | PRIMARY | [7 empty] | SERVICE |  | BACKFEED |  |  | SECONDARY |  | CONSTRUCTION |  | RIGHT
LOCATION |  | ANGLE |  |  | Back | POLE |  | ASSEMBLY |  | GUYS |  | ANCHORS |  | XFMRS |  |  |  | Back |  |  | SERVICE |  | UNITS |  | OF
NUMBER | STATION | (DEG) | No. | SIZE/TYPE | Span | HEIGHT | CLASS | No. | Units | No. | Units | No. | Units | No. | Units | No. | SIZE/TYPE | Span | No. | SIZE/TYPE | No. | Units | No. | Units | WAY | REMARKS/COMMENTS/NOTES | ACSR | #4/0 Triplex | #2 Triplex
|  |  | 4 | #2 ACSR | 50 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1.
1 | [7 empty] | 1 | C5.21
|  |  | 4 | #2 ACSR | 20 | 40 | 4 | 1 | C6.21 |  |  |  |  | 1 | G3.3-75 | 1 | #4/0 |  |  |  | 1 | J3.1 | 1 | H1.1 |  | SEE NOTES 1, 2,6, AND 12.
0 | [7 empty] | 1 | S1.3 | [5 empty] | 277/480V |  | QUADRUPLEX | [8 empty] | STEP-UP TRANSFORMER BANK.
[15 empty] | 3-PHASE | [10 empty] | ADDITIONAL NOTES ON DRAWING.
|  |  | 4 | #2 ACSR | 20 | 40 | 4 | 1 | S2.31 | [13 empty] | 1 | H1.1 |  | SEE NOTES 1,6,AND 10. | 80 | 0 | 0
T92 | [7 empty] | 1 | R3.3a | [16 empty] | ADDITIONAL NOTES ON DRAWING.
VACUUM SWITCH
|  |  | 4 | #2 ACSR | 20 | 40 | 4 | 1 | C1.11 | [11 empty] | 1 | J3.1 | 1 | H1.1 |  | SEE NOTES 1,4, 6, AND 11. | 80 | 0 | 0
T91 | [7 empty] | 1 | Q4.1a | [16 empty] | SEE DETAILS ON PLANS.
METERING POLE.
ADDITIONAL NOTES ON DRAWING.
|  |  | 4 | #2 ACSR | 175 | 40 | 4 | 1 | C6.21 | [11 empty] | 1 | J3.1 | 1 | H1.1 |  | SEE NOTES 1, AND 6. | 700 | 0 | 0
T90 | [7 empty] | 1 | S2.32a | [13 empty] | 1 | H4.1a |  | SEE DETAILS ON PLANS.
LOAD BREAK SWITCH
ADDITIONAL NOTES ON DRAWING.
|  |  | 4 | #2 ACSR | 105 | 40 | 4 | 1 | C1.11 |  |  |  |  | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1 AND 2.
1-1 | [14 empty] | 120/240V | [5 empty] | 1 | J3.1 |  |  |  | ONE SERVICE.
1-PHASE
[6 empty] | 30 | 4 | [8 empty] | 1 | #4 TRIPLEX |  |  |  | 1 | Q2.1G | 1 | H1.1 |  | SEE NOTES 1 AND 3.
1-1-1 | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 180 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1.
1-2
|  |  | 4 | #2 ACSR | 115 | 40 | 4 | 1 | C1.11 |  |  |  |  | 1 | G1.4-10 | 2 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1 AND 2. | 460 | 0 | 150
2 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1 |  |  |  | TWO SERVICES.
1-PHASE
|  | 5 | 4 | #2 ACSR | 140 | 40 | 4 | 1 | C2.21 | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1. | 560 | 0 | 0
3
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [12 empty] | SEE NOTE 1. | 640 | 0 | 0
4
|  | 10 | 4 | #2 ACSR | 155 | 40 | 4 | 1 | C2.21 | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1. | 620 | 0 | 0
5
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 1 | C1.11 | 2 | E1.1La | 2 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 640 | 0 | 0
6 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1
1-PHASE
[6 empty] | 40 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 85 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 85 | 0
6A
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 100 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 100 | 75
6B | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 130 | 40 | 4 | 1 | C1.11 | [8 empty] | 130 | 1 | #6 DUPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 520 | 130 | 0
7
|  |  | 4 | #2 ACSR | 130 | 40 | 4 | 1 | C1.11 | [8 empty] | 130 | 1 | #6 DUPLEX | 1 | J3.1 |  |  |  | SEE NOTE 1. | 520 | 130 | 0
8 | [25 empty] | INSTALL STREET LIGHT.
|  |  | 4 | #2 ACSR | 130 | 40 | 4 | 1 | C5.21 | [13 empty] | 1 | H1.1 |  | SEE NOTES 1, 3, AND 6. | 520 | 0 | 0
9 | [7 empty] | 1 | C1.11
|  |  | 4 | #2 ACSR | 25 | 40 | 4 | 1 | C6.21 | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTES 1 AND 7. | 100 | 0 | 0
9-1 | [7 empty] | 1 | S1.3 | [16 empty] | PROVIDE #2 ACSR JUMPERS.
[8 empty] | 2 | A2.021
[8 empty] | 1 | A1.01
|  |  | 4 | #2 ACSR | 115 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTE 1. | 460 | 0 | 0
9-2
|  |  | 4 | #2 ACSR | 140 | 40 | 4 | 1 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 2 | N6.1a |  | SEE NOTE 1. | 560 | 0 | 0
9-3 | [7 empty] | 2 | A5.01
|  |  | 2 | #2 ACSR | 85 | 40 | 4 | 1 | A2.1 | 2 | E1.1La | 2 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 170 | 0 | 0
9-3-1 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1
1-PHASE
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 147 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 147 | 75
9-3-1A | [25 empty] | ONE SERVICE.
|  |  | 2 | #2 ACSR | 110 | 40 | 4 | 1 | A2.1 | 2 | E1.1La | 2 | F7.0 |  |  | 1 | #4 TRIPLEX | 110 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 220 | 110 | 75
9-3-2
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 97 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 97 | 75
9-3-2A | [25 empty] | ONE SERVICE.
|  |  | 2 | #2 ACSR | 195 | 40 | 4 | 1 | A2.1 | 2 | E1.1La | 2 | F7.0 |  |  | 2 | #4 TRIPLEX | 195 | 1 | #1/0 TRIPLEX | 3 | J3.1 |  |  |  | SEE NOTES 1 AND 6. | 390 | 195 | 150
9-3-3 | [25 empty] | TWO SERVICES.
PROVIDE #2 ACSR JUMPERS.
|  | 34 | 2 | #2 ACSR | 192 | 40 | 4 | 2 | A5.1 | 2 | E1.1La | 2 | F7.0 | 1 | G1.4-15 | 1 | #4 TRIPLEX | 192 | 1 | #1/0 TRIPLEX | 3 | J3.1 | 1 | N6.1a |  | SEE NOTES 1 AND 2.
9-3-4 | [7 empty] | 1 | A1.04N | [5 empty] | 120/240V | [7 empty] | 1 | H1.1 |  | ONE SERVICE.
[15 empty] | 1-PHASE | [10 empty] | PROVIDE #2 ACSR JUMPERS.
|  |  | 2 | #2 ACSR | 90 | 40 | 4 | 1 | A2.1 | [8 empty] | 90 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
9-3-5
|  | 5 | 2 | #2 ACSR | 170 | 40 | 4 | 1 | A2.3 | 2 | E1.1La | 2 | F7.0 |  |  |  |  | 170 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTES 1 AND 2. | 340 | 170 | 0
9-3-6 | [25 empty] | PROVIDE #2 ACSR JUMPERS.
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 85 | 1 | #1/0 TRIPLEX | 1 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 85 | 75
9-3-6A | [25 empty] | ONE SERVICE.
|  | 7 | 2 | #2 ACSR | 220 | 40 | 4 | 2 | A5.1 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6. | 440 | 0 | 0
9-3-7 | [7 empty] | 1 | S1.1
|  |  | 2 | #2 ACSR | 200 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 400 | 0 | 0
9-3-8
|  |  | 2 | #2 ACSR | 160 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1.
9-3-9
|  |  | 2 | #2 ACSR | 200 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1.
9-3-10
|  |  | 2 | #2 ACSR | 200 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 400 | 0 | 0
9-3-11
|  |  | 2 | #2 ACSR | 180 | 40 | 4 | 2 | A5.1 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6. | 360 | 0 | 0
9-3-12
|  |  | 2 | #2 ACSR | 215 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 430 | 0 | 0
9-3-13
|  |  | 2 | #2 ACSR | 215 | 40 | 4 | 2 | A5.1 | 2 | E1.1La | 2 | F7.0 | [12 empty] | SEE NOTE 1. | 430 | 0 | 0
9-3-14
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 2 | A5.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-15 | [25 empty] | PROVIDE #2 ACSR JUMPERS.
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [13 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6. | 550 | 0 | 0
9-3-16
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-17
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-18
|  |  | 2 | #2 ACSR | 245 | 40 | 4 | 1 | A2.1 | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 490 | 0 | 0
9-3-19 | [14 empty] | 120/240V | [5 empty] | 1 | J3.1
1-PHASE
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 120 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 120 | 75
9-3-19A
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-20
|  | 3 | 2 | #2 ACSR | 240 | 40 | 4 | 1 | A2.3P | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1. | 480 | 0 | 0
9-3-21
|  | 13 | 2 | #2 ACSR | 240 | 40 | 4 | 1 | A2.3P | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1. | 480 | 0 | 0
9-3-22
|  | 7 | 2 | #2 ACSR | 165 | 40 | 4 | 1 | A2.3P | 1 | E1.1La | 1 | F7.0 | [12 empty] | SEE NOTE 1. | 330 | 0 | 0
9-3-23
|  |  | 2 | #2 ACSR | 277 | 40 | 4 | 1 | A2.1 | [13 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6. | 554 | 0 | 0
9-3-24
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-25
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-26
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 550 | 0 | 0
9-3-27
|  |  | 2 | #2 ACSR | 275 | 40 | 4 | 1 | A2.1 | [13 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6.
9-3-28
|  |  | 2 | #2 ACSR | 240 | 40 | 4 | 2 | A5.1 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1 |  | SEE NOTES 1 AND 6.
9-3-29
|  | 11 | 2 | #2 ACSR | 155 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1.
9-3-30
|  |  | 2 | #2 ACSR | 140 | 40 | 4 | 1 | A5.1 | 1 | E1.1La | 1 | F7.0 | 1 | G1.5-10 | 1 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 280 | 0 | 75
9-3-31 | [14 empty] | 120/240V | [5 empty] | 1 | J3.1
1-PHASE
|  |  | 2 | #2 ACSR | 180 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 360 | 0 | 0
9-4
|  |  | 2 | #2 ACSR | 115 | 40 | 4 | 1 | A2.1 | [16 empty] | SEE NOTE 1. | 230 | 0 | 0
9-5
|  | 19 | 2 | #2 ACSR | 145 | 40 | 4 | 1 | A3.1 | 1 | E1.1La | 1 | F7.0 | [7 empty] | 1 | N5.2 |  |  |  | SEE NOTE 1. | 290 | 0 | 0
9-6 | [25 empty] | PROVIDE #2 ACSR JUMPERS.
|  |  | 2 | #2 ACSR | 130 | 40 | 4 | 1 | A5.1 | 1 | E1.1La | 1 | F7.0 | 1 | G1.5-10 | 1 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2 AND 6. | 260 | 0 | 75
9-7 | [14 empty] | 120/240V | [5 empty] | 1 | K3.1 |  |  |  | NEW OVERHEAD SERVICE.
1-PHASE
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTE 1. | 640 | 0 | 0
10
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 130 | 1 | #6 DUPLEX | 1 | J3.1 |  |  |  | SEE NOTE 1. | 640 | 130 | 0
11 | [7 empty] | 1 | C5.21 | [16 empty] | INSTALL STREET LIGHT.
|  |  | 4 | #2 ACSR | 130 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-37.5 | 1 | #1/0 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2 AND 6.
11-1 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1 |  |  |  | SCHOOL SINGLE-PHASE SERVICE.
1-PHASE
|  |  | 4 | #2 ACSR | 40 | 40 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [12 empty] | SEE NOTE 1. | 160 | 0 | 0
12
|  |  | 4 | #2 ACSR | 190 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-15 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6.
13 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1
1-PHASE
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 85 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 85 | 75
13-1 | [25 empty] | ONE SERVICE.
INSTALL STREET LIGHT.
|  |  | 4 | #2 ACSR | 76 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  | 2 | #4 TRIPLEX | 76 | 1 | #1/0 TRIPLEX | 3 | J3.1 |  |  |  | SEE NOTE 1. | 304 | 76 | 150
14 | [25 empty] | ONE SERVICE.
INSTALL STREET LIGHT.
[6 empty] | 40 | 4 | [8 empty] | 1 | #4 TRIPLEX | 45 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 45 | 75
14-1 | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 65 | 40 | 4 | 1 | C6.21 | [16 empty] | SEE NOTE 1. | 260 | 0 | 0
15 | [7 empty] | 1 | C1.11 | [16 empty] | INSTALL STREET LIGHT
[8 empty] | 1 | A1.01 | [16 empty] | UNIT C6.21 ON TOP
[8 empty] | 2 | A2.021 | [16 empty] | INSTALL #2 JUMPERS.
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 | [7 empty] | 3 | J3.1 |  |  |  | SEE NOTE 1. | 640 | 0 | 0
15A-1 | [25 empty] | ONE SERVICE.
INSTALL STREET LIGHT.
[6 empty] | 40 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 105 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 105 | 75
15A-1A | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 80 | 40 | 4 | 1 | C1.11 |  |  |  |  | 1 | G1.4-10 |  |  | 80 | 1 | #1/0 TRIPLEX | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 320 | 80 | 0
15A-2 | [14 empty] | 120/240V | [5 empty] | 3 | J3.1
1-PHASE
[6 empty] | 35 | 4 | [8 empty] | 1 | #4 TRIPLEX | 70 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15A-2A | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 75 | 40 | 4 | 1 | C1.11 | [6 empty] | 2 | #4 TRIPLEX | 75 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15A-3 | [25 empty] | TWO SERVICES.
|  |  | 4 | #2 ACSR | 135 | 40 | 4 | 1 | C1.11 |  |  |  |  | 1 | G1.4-10 | 2 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6.
15A-4 | [14 empty] | 120/240V | [5 empty] | 3 | J3.1 |  |  |  | TWO SERVICES.
[15 empty] | 1-PHASE | [10 empty] | INSTALL STREET LIGHT.
[6 empty] | 35 | 4 | [8 empty] | 3 | #4 TRIPLEX |  | 1 | #1/0 TRIPLEX | 4 | J3.1 |  |  |  | SEE NOTE 1.
15A-4A | [25 empty] | THREE SERVICES.
|  |  | 4 | #2 ACSR | 120 | 40 | 4 | 1 | C5.21 | 2 | E7.1 | 2 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2 AND 6.
15A-5 | [7 empty] | 1 | A5.01 | [5 empty] | 120/240V | [10 empty] | INSTALL STREET LIGHT.
1-PHASE
[6 empty] | 40 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 80 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15A-5A | [20 empty] | 1 |  |  |  |  | ONE SERVICE.
|  |  | 4 | #2 ACSR | 50 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 50 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15A-6
[6 empty] | 35 | 4 | [8 empty] | 2 | #4 TRIPLEX | 80 | 1 | #2 TRIPLEX | 4 | J3.1 |  |  |  | SEE NOTE 1.
15A-6A | [25 empty] | TWO SERVICES.
INSTALL STREET LIGHT.
|  |  | 4 | #2 ACSR | 170 | 40 | 4 | 1 | C1.11 |  |  |  |  | 1 | G1.4-15 | 1 | #2 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2 AND 6. | 680 | 0 | 75
15B-1 | [14 empty] | 120/240V | [5 empty] | 3 | J3.1 |  |  |  | INSTALL STREET LIGHT
1-PHASE
[6 empty] | 35 | 4 | [8 empty] | 2 | #4 TRIPLEX | 120 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 120 | 150
15B-1A | [25 empty] | TWO SERVICES.
|  |  | 4 | #2 ACSR | 65 | 40 | 4 | 1 | C1.11 | [8 empty] | 140 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 260 | 140 | 0
15B-2
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 110 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 110 | 75
15B-2A | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 85 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTE 1. | 340 | 0 | 0
15B-3
|  |  | 4 | #2 ACSR | 85 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTE 1. | 340 | 0 | 0
15B-4
|  |  | 4 | #2 ACSR | 95 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6.
15B-5 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1
1-PHASE
[6 empty] | 35 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 115 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15B-5A | [25 empty] | ONE SERVICE.
[6 empty] | 35 | 4 |  |  | 1 | E1.4L | 1 | F7.0 | [12 empty] | SEE NOTE 1.
15B-5B
|  |  | 4 | #2 ACSR | 95 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 95 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
15B-6 | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 30 | 40 | 3 | 1 | C1.11 |  |  |  |  | 1 | G1.4-100 | 2 | #4/0 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, 6, 8, AND 9. | 120 | 0 | 150
16 | [14 empty] | 120/240V | [5 empty] | 1 | J3.1 |  |  |  | TEMPORARY STEP UP TRANSFORMER.
1-PHASE
|  |  | 4 | #2 ACSR | 90 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-10 | 1 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 360 | 0 | 75
17 | [14 empty] | 120/240V | [5 empty] | 3 | J3.1 |  |  |  | ONE SERVICE.
1-PHASE
[6 empty] | 40 | 4 | [8 empty] | 2 | #4 TRIPLEX | 90 | 2 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 90 | 150
17A | [25 empty] | TWO SERVICES.
[6 empty] | 35 | 4 | [8 empty] | 2 | #4 TRIPLEX | 90 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 90 | 150
17B | [25 empty] | ONE SERVICE.
|  |  | 4 | #2 ACSR | 100 | 40 | 4 | 1 | C1.11 | [6 empty] | 1 | #4 TRIPLEX | 100 | 1 | #1/0 TRIPLEX | 3 | J3.1 |  |  |  | SEE NOTE 1. | 400 | 100 | 75
18 | [25 empty] | ONE SERVICE.
|  | 3 | 4 | #2 ACSR | 95 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 95 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
19 | [7 empty] | 1 | C6.21 | [16 empty] | INSTALL STREET LIGHT.
[8 empty] | 2 | A2.021
[8 empty] | 1 | A1.01
|  |  | 4 | #2 ACSR | 160 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 1 | N7.6 |  |  |  | SEE NOTES 1, 2, AND 6. | 640 | 0 | 75
19-1 | [20 empty] | 3 | J3.1 |  |  |  | ONE SERVICE.
|  |  | 4 | #2 ACSR | 125 | 40 | 4 | 1 | C1.11 | 1 | E7.1 | 1 | F7.0 | 1 | G1.4-10 |  |  | 125 | 1 | #1/0 TRIPLEX | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6. | 500 | 125 | 0
19-2 | [14 empty] | 120/240V | [5 empty] | 3 | J3.1
1-PHASE
[6 empty] | 40 | 4 | [8 empty] | 2 | #4 TRIPLEX | 90 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1. | 0 | 90 | 150
19-2A | [25 empty] | TWO SERVICES.
|  |  | 4 | #2 ACSR | 125 | 40 | 4 | 1 | C5.21 | 1 | E1.1La | 1 | F7.0 |  |  | 2 | #4 TRIPLEX | 125 | 1 | #1/0 TRIPLEX | 2 | J3.1 | 1 | H1.1 |  | SEE NOTES 1 AND 2. | 500 | 125 | 150
19-3 | [25 empty] | TWO SERVICES.
|  |  | 4 | #2 ACSR | 110 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTE 1.
20
|  |  | 4 | #2 ACSR | 110 | 40 | 4 | 1 | C1.11 | 1 | E7.1 | 1 | F7.0 | 1 | G1.4-10 | 1 | #4 TRIPLEX |  |  |  | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6.
21 | [14 empty] | 120/240V | [5 empty] | 2 | J3.1 |  |  |  | INSTALL STREET LIGHT.
[15 empty] | 1-PHASE | [10 empty] | ONE SERVICE.
[6 empty] | 40 | 4 |  |  | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX | 135 | 1 | #2 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
21A
|  |  | 4 | #2 ACSR | 125 | 40 | 4 | 1 | C1.11 | [16 empty] | SEE NOTES 1. | 500 | 0 | 0
22
|  |  | 4 | #2 ACSR | 100 | 40 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 2 | J3.1 |  |  |  | SEE NOTE 1.
23 | [25 empty] | ONE SERVICE.
INSTALL STREET LIGHT.
|  | 19 | 4 | #2 ACSR | 100 | 40 | 4 | 1 | C2.21 | 1 | E7.1 | 1 | F7.0 |  |  |  |  | 100 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
24
|  |  | 4 | #2 ACSR | 80 | 40 | 4 | 1 | C5.21 |  |  |  |  | 1 | G1.5-10 | 2 | #4 TRIPLEX | 100 | 1 | #1/0 TRIPLEX | 1 | N7.6 | 1 | H1.1 |  | SEE NOTES 1, 2, AND 6.
25 | [14 empty] | 120/240V | [5 empty] | 4 | J3.1 |  |  |  | TWO SERVICES.
1-PHASE
[6 empty] | 40 | 4 | [8 empty] | 1 | #4 TRIPLEX | 80 | 1 | #2 TRIPLEX | 1 | J3.1 |  |  |  | SEE NOTE 1.
25A
STAKING SHEET NOTES:
1. SEE PROJECT DETAIL DRAWINGS FOR MODIFIED RUS CONSTRUCTION UNITS. UNLESS OTHERWISE INDICATED, GUY LEADS SHALL BE 30 FEET.
2. On the RUS Construction Unit G1.2 and G1.3 an armor rod is indicated at the connection to the line with a hot line clamp. do not install surge arresters on transformers.
3. POSITION POLE SUCH THAT THE EXISTING TANK FARM FEEDER CAN EXTEND UP TO THE NEW METER WITHOUT SPLICING. EXTEND THE FEEDER UP TO THE NEW METER USING GALVANIZED RIDGID CONDUIT.
MATCH EXISTING CONDUIT SIZE.
4. INSTALL BILL OF MATERIAL ITEM 2, GREEN LIGHT, TO INDICATE POWER AVAILABLE FROM TOGIAK. INSTALL 1'-0" BELOW THE NEUTRAL CONDUCTOR. CONNECT THE LIGHT TO THE 120 VOLT FROM A-PHASE POTENTIAL TRANSFORMER.
5. REPLACE THE EXISTING METER BASE AND METER AS INDICATED ON THE DRAWINGS.
6. RUS ASSEMBLY H1.1 SHALL USE #4 AWG COPPER FOR POLE GROUND CONDUCTOR. ALUMINUM CONDUCTORS SHALL NOT BE USED.
7. INSTALL 25T FUSE LINK IN CUTOUTS FOR TAP.
8. INSTALL NEW SERVICE DROP FROM TRANSFORMER TO EXISTING SERVICE RISER AT POWER PLANT.
9. INSTALL JUMPERS BETWEEN THE THREE PRIMARY PHASES TO CREATE A SINGLE-PHASE SYSTEM THROUGHOUT THE COMMUNITY. JUMPERS ARE TO BE REMOVED WHEN THE THREE-PHASE TIE IS COMPLETED AND THE COMMUNITY POWERED AT THREE-PHASE. INSTALL #2 AWG JUMPERS WITH HOT LINE CLAMPS AND ARMOR ROD.
10. INSTALL MULTI-CONDUCTOR CABLE FOR VACUUM SWITCH CONTROL TO MODULE.
11. INSTALL 4/C#10 AWG MULTI-CONDUCTOR CABLE FOR THE CURRENT TRANSFORMER LEADS AND 4/C #12 AWG FOR THE POTENTIAL TRANSFORMER LEADS TO THE MODULE.
12. PROVIDE SOLID BLADE CUTOUTS FOR RUS UNIT S1.3. CONNECT FUSED CUTOUTS SUCH THAT THE LOAD SIDE IS TWIN HILLS DISTRIBUTION SYSTEM.

## Sheet1
Point Number | Raw Description | Style
38 | 1G-1A | POLE P
34 | 1G-2 | EPOLE-P
37 | 1G-3 | POLE P
36 | 1H | EPOLE-P
43 | 1H-1 | EPOLE-P
48 | 1H-1A | POLE P
42 | 1H-2 | EPOLE-P
45 | 1H-2A | POLE P
44 | 1H-2B | POLE P
41 | 1H-3 | EPOLE-P
46 | 1H-3A | POLE P
39 | 1H-4 | EPOLE-P
40 | 1H-4A | POLE P
47 | 1H-4B | POLE P
49 | 1I | EPOLE-P
50 | 1J | EPOLE-P
52 | 1J-1 | EPOLE-P
51 | 1K | EPOLE-P
17 | 2 | EPOLE-P
18 | 2A | EPOLE-P
10 | 2B | EPOLE-P
74 | 2B-1 | EPOLE-P
16 | 2B-2 | EPOLE-P
19 | 2B-2A | POLE P
68 | 2B-2B-1 | POLE P
11 | 2C | EPOLE-P
12 | 2D | EPOLE-P
73 | 2D-1 | POLE P
14 | 2D-2 | POLE P
6 | 2E | EPOLE-P
7 | 2F | EPOLE-P
8 | 2G | EPOLE-P
114 | 2H | EPOLE-P
72 | 2H-1 | POLE P
71 | 2H-2 | POLE P
2 | 2I | EPOLE-P
3 | 2J | EPOLE-P
1 | 2K | EPOLE-P
226 | 2K-1A | POLE P
4 | 2K-1B | POLE P
20 | 3 | EPOLE-P
53 | 4 | EPOLE-P
55 | 5 | EPOLE-P
56 | 6 | EPOLE-P
54 | 7 | EPOLE-P
57 | 8 | EPOLE-P
58 | 9 | EPOLE-P
59 | 10 | EPOLE-P
64 | 11 | EPOLE-P
65 | 12 | EPOLE-P
66 | 15A | POLE P

## Sheet2
Point Number | Raw Description | Style
5 | 2E-2 | POLE P
70 | 2E-1 | POLE P
77 | 1* | EPOLE-P
23 | 1A | EPOLE-P
76 | 1B | EPOLE-P
75 | 1C | EPOLE-P
24 | 1C-1A | POLE P
25 | 1C-1B | POLE P
26 | 1D | EPOLE-P
28 | 1D-1A | POLE P
27 | 1D-1B | POLE P
29 | 1E | EPOLE-P
30 | 1F | EPOLE-P
31 | 1F-1 | POLE P
32 | 1F-2 | POLE P
33 | 1G | EPOLE-P
35 | 1G-1 | EPOLE-P
38 | 1G-1A | POLE P
34 | 1G-2 | EPOLE-P
37 | 1G-3 | POLE P
36 | 1H | EPOLE-P
43 | 1H-1 | EPOLE-P
48 | 1H-1A | POLE P
42 | 1H-2 | EPOLE-P
45 | 1H-2A | POLE P
44 | 1H-2B | POLE P
41 | 1H-3 | EPOLE-P
46 | 1H-3A | POLE P
39 | 1H-4 | EPOLE-P
40 | 1H-4A | POLE P
47 | 1H-4B | POLE P
49 | 1I | EPOLE-P
50 | 1J | EPOLE-P
52 | 1J-1 | EPOLE-P
51 | 1K | EPOLE-P
17 | 2 | EPOLE-P
18 | 2A | EPOLE-P
10 | 2B | EPOLE-P
74 | 2B-1 | EPOLE-P
16 | 2B-2 | EPOLE-P
19 | 2B-2A | POLE P
68 | 2B-2B-1 | POLE P
11 | 2C | EPOLE-P
12 | 2D | EPOLE-P
73 | 2D-1 | POLE P
14 | 2D-2 | POLE P
6 | 2E | EPOLE-P
7 | 2F | EPOLE-P
8 | 2G | EPOLE-P
114 | 2H | EPOLE-P
72 | 2H-1 | POLE P
71 | 2H-2 | POLE P
2 | 2I | EPOLE-P
3 | 2J | EPOLE-P
1 | 2K | EPOLE-P
226 | 2K-1A | POLE P
4 | 2K-1B | POLE P
20 | 3 | EPOLE-P
53 | 4 | EPOLE-P
55 | 5 | EPOLE-P
56 | 6 | EPOLE-P
54 | 7 | EPOLE-P
57 | 8 | EPOLE-P
58 | 9 | EPOLE-P
59 | 10 | EPOLE-P
64 | 11 | EPOLE-P
65 | 12 | EPOLE-P
66 | 15A | POLE P

## Sheet3
Point Number | Easting | Northing | Raw Description | Style
23 | 1477591.84' | 2178074.23' | 1A | EPOLE-P
76 | 1477497.51' | 2178138.62' | 1B | EPOLE-P
75 | 1477454.21' | 2178168.30' | 1C | EPOLE-P
24 | 1477559.44' | 2178220.60' | 1C-1A | POLE P
25 | 1477487.58' | 2178279.34' | 1C-1B | POLE P
26 | 1477343.52' | 2178167.36' | 1D | EPOLE-P
28 | 1477397.78' | 2178084.36' | 1D-1A | POLE P
27 | 1477320.78' | 2178264.26' | 1D-1B | POLE P
29 | 1477199.06' | 2178148.43' | 1E | EPOLE-P
30 | 1477051.55' | 2178129.10' | 1F | EPOLE-P
31 | 1477069.40' | 2177995.83' | 1F-1 | POLE P
32 | 1477041.33' | 2177901.19' | 1F-2 | POLE P
33 | 1476969.53' | 2178118.35' | 1G | EPOLE-P
35 | 1476968.04' | 2178267.00' | 1G-1 | EPOLE-P
38 | 1477085.84' | 2178264.80' | 1G-1A | POLE P
34 | 1476966.12' | 2178459.82' | 1G-2 | EPOLE-P
37 | 1477050.15' | 2178456.24' | 1G-3 | POLE P
36 | 1476805.73' | 2178096.90' | 1H | EPOLE-P
43 | 1476773.58' | 2178221.12' | 1H-1 | EPOLE-P
48 | 1476816.52' | 2178005.99' | 1H-1A | POLE P
42 | 1476751.81' | 2178305.13' | 1H-2 | EPOLE-P
45 | 1476639.60' | 2178252.06' | 1H-2A | POLE P
44 | 1476516.73' | 2178192.44' | 1H-2B | POLE P
41 | 1476737.09' | 2178360.17' | 1H-3 | EPOLE-P
46 | 1476808.72' | 2178401.30' | 1H-3A | POLE P
39 | 1476703.40' | 2178492.14' | 1H-4 | EPOLE-P
40 | 1476571.76' | 2178434.60' | 1H-4A | POLE P
47 | 1476816.07' | 2178541.58' | 1H-4B | POLE P
49 | 1476625.29' | 2178073.24' | 1I | EPOLE-P
50 | 1476457.30' | 2178051.22' | 1J | EPOLE-P
52 | 1476477.46' | 2177974.63' | 1J-1 | EPOLE-P
51 | 1476306.67' | 2178031.54' | 1K | EPOLE-P
77 | 1477789.11' | 2178012.76' | 1* | EPOLE-P
17 | 1477937.18' | 2177992.64' | 2 | EPOLE-P
18 | 1477925.39' | 2178135.60' | 2A | EPOLE-P
10 | 1477913.70' | 2178278.69' | 2B | EPOLE-P
74 | 1477810.16' | 2178292.44' | 2B-1 | EPOLE-P
16 | 1477706.62' | 2178306.19' | 2B-2 | EPOLE-P
19 | 1477615.73' | 2178362.46' | 2B-2A | POLE P
68 | 1477696.29' | 2178450.58' | 2B-2B-1 | POLE P
11 | 1477993.42' | 2178541.89' | 2C | EPOLE-P
12 | 1478073.13' | 2178805.08' | 2D | EPOLE-P
73 | 1477929.36' | 2178827.80' | 2D-1 | POLE P
14 | 1477785.63' | 2178850.56' | 2D-2 | POLE P
6 | 1478152.84' | 2179068.27' | 2E | EPOLE-P
5 | 1477909.20' | 2179077.57' | 2E-2 | POLE P
70 | 1478031.02' | 2179072.92' | 2E-1 | POLE P
7 | 1478204.02' | 2179237.24' | 2F | EPOLE-P
8 | 1478090.58' | 2179431.55' | 2G | EPOLE-P
114 | 1477976.82' | 2179626.42' | 2H | EPOLE-P
72 | 1477864.79' | 2179644.36' | 2H-1 | POLE P
71 | 1477752.44' | 2179662.85' | 2H-2 | POLE P
2 | 1477863.06' | 2179821.28' | 2I | EPOLE-P
3 | 1477700.64' | 2179973.28' | 2J | EPOLE-P
1 | 1477545.15' | 2180118.79' | 2K | EPOLE-P
226 | 1477459.43' | 2180088.12' | 2K-1A | POLE P
4 | 1477667.53' | 2180257.47' | 2K-1B | POLE P
20 | 1478137.14' | 2177920.01' | 3 | EPOLE-P
53 | 1478920.41' | 2177338.55' | 4 | EPOLE-P
55 | 1479100.85' | 2177268.55' | 5 | EPOLE-P
56 | 1479285.95' | 2177196.72' | 6 | EPOLE-P
54 | 1479443.16' | 2177135.76' | 7 | EPOLE-P
57 | 1479557.47' | 2177048.78' | 8 | EPOLE-P
58 | 1479651.29' | 2176910.61' | 9 | EPOLE-P
59 | 1479755.73' | 2176740.63' | 10 | EPOLE-P
64 | 1479883.80' | 2176613.43' | 11 | EPOLE-P
65 | 1480008.75' | 2176600.33' | 12 | EPOLE-P
66 | 1480715.14' | 2176545.77' | 15A | POLE P