## STAKSHT
REV. NO. | DATE | DESCRIPTION | [6 empty] | BY | [12 empty] | DESIGNER |  | DATE
0 | 2018-01-26 | ISSUED FOR CONSTRUCTION. | [6 empty] | CWV | GRAY STASSEL ENGINEERING, INC. | [11 empty] | CWV |  | 2018-01-26 |  | TWIN HILLS RURAL POWER
1 | 2018-10-03 | REVISED PER ADDENDA 1 | [6 empty] | TRK | 1309 EAST KLATT ROAD, SUITE C | [11 empty] | CHECKER |  | DATE |  | SYSTEM UPGRADE
[10 empty] | ANCHORAGE, ALASKA 99511 | [11 empty] | CWV |  | 2018-01-26 |  | TOGIAK TO TWIN HILLS TIE-LINE
[10 empty] | (907) 349-0100 | [11 empty] | DIST. ENG. |  | DATE |  |  |  |  | Total ACSR = | 60600 | FEET
[22 empty] | CWV |  | 2018-01-26 |  |  |  |  | Total #4/0 Triplex = | 0 | FEET
[29 empty] | Estimated #2 Triplex = | 300 | FEET
[18 empty] | SECONDARY CONDUCTOR |  |  |  |  | MISCELLANEOUS
|  | LINE | CONDUCTOR |  |  |  |  | PRIMARY | [7 empty] | SERVICE |  | BACKFEED |  |  | SECONDARY |  | CONSTRUCTION |  | RIGHT
LOCATION |  | ANGLE |  |  | Back | POLE |  | ASSEMBLY |  | GUYS |  | ANCHORS |  | XFMRS |  |  |  | Back |  |  | SERVICE |  | UNITS |  | OF
NUMBER | STATION | (DEG) | No. | SIZE/TYPE | Span | HEIGHT | CLASS | No. | Units | No. | Units | No. | Units | No. | Units | No. | SIZE/TYPE | Span | No. | SIZE/TYPE | No. | Units | No. | Units | WAY | REMARKS/COMMENTS/NOTES | ACSR | #4/0 Triplex | #2 Triplex
[6 empty] | 45 | 4 | 1 | C1.11 | [11 empty] | 1 | J3.1 | 1 | H1.1 |  | SEE NOTES 1 & 2.
10 | [7 empty] | 1 | C5.21 | [16 empty] | DIRECT BURY POLE.
|  |  | 4 | #2 ACSR | 20 | 45 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 20 | 1 | #1/0 TRIPLEX | [5 empty] | SEE NOTE 1.
10-1 | [25 empty] | DIRECT BURY POLE.
SLACK SPAN BACK TO LOCATION 10.
|  |  | 4 | #2 ACSR | 79 | 45 | 4 | 1 | C1.11 | [8 empty] | 79 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
10-2 | [25 empty] | DIRECT BURY POLE.
|  |  | 4 | #2 ACSR | 110 | 45 | 4 | 1 | C1.11 | [8 empty] | 110 | [7 empty] | SEE NOTE 1.
10-3 | [25 empty] | DIRECT BURY POLE.
|  |  | 4 | #2 ACSR | 150 | 45 | 4 | 1 | C1.11 | [8 empty] | 150 | 1 | #1/0 TRIPLEX | 2 | J3.1 | 1 | H1.1 |  | SEE NOTE 1.
10-4 | [25 empty] | DIRECT BURY POLE.
|  |  | 4 | #2 ACSR | 130 | 45 | 4 | 1 | C1.11 | [8 empty] | 130 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
10-5 | [25 empty] | DIRECT BURY POLE.
|  | 18 | 4 | #2 ACSR | 50 | 45 | 4 | 1 | C2.21P | [8 empty] | 50 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
10-6 | [25 empty] | DIRECT BURY POLE.
[10 empty] | 1 | E1.4L | 1 | F7.0 | [12 empty] | SEE NOTE 1.
10-6A | [5 empty] | 40 | 4 | [18 empty] | DIRECT BURY POLE.
|  |  | 4 | #1/0 ACSR | 135 | 45 | 4 | 1 | C1.11 | 1 | E1.1La | 1 | F7.0 |  |  |  |  | 135 | 1 | #1/0 TRIPLEX | 2 | J3.1 |  |  |  | SEE NOTE 1.
10-7 | [25 empty] | DIRECT BURY POLE.
|  |  | 4 | #1/0 ACSR | 215 | 40 | 4 | 1 | C6.21 | 1 | E1.1La | 1 | F7.0 | [5 empty] | 1 | #1/0 TRIPLEX | 1 | J3.1 | 1 | H1-PILE |  | SEE NOTE 1.
T1 | [7 empty] | 1 | S2.32b | [13 empty] | 1 | H1.1G |  | FIRST PILE SUPPORT.
[23 empty] | 1 | P3.3G |  | LOAD BREAK SWITCH.
[23 empty] | 1 | H4.1a
|  |  | 4 | #1/0 ACSR | 20 | 40 | 4 | 1 | C1.11 | [11 empty] | 1 | J3.1 | 1 | H1-PILE |  | SEE NOTE 1.
T2 | [7 empty] | 1 | Q4.1b | [16 empty] | METERING POLE.
|  |  | 4 | #1/0 ACSR | 20 | 40 | 4 | 1 | S2.31 | [8 empty] | 20 | 1 | #6 AWG | 1 | J3.1 | 1 | H1-PILE |  | SEE NOTE 1.
T3 | [7 empty] | 1 | R3.3b | [10 empty] | QUADRUPLEX |  |  | 1 | P3.3G |  | RECLOSER.
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T4 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 280 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1120 | 0 | 0
T5 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 280 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1120 | 0 | 0
T6 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 280 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1120 | 0 | 0
T7 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1200 | 0 | 0
T8 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T9 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T10 | [22 empty] | 1 | P3.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T11 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1200 | 0 | 0
T12 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T13 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T14 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T15 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T16 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T17 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T18 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T19 | [22 empty] | 1 | P3.1G
|  | 42 | 4 | #1/0 ACSR | 255 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1020 | 0 | 0
T20 | [22 empty] | 1 | P3.3G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T21 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T22 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T23 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T24 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T25 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T26 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T27 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 120 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 480 | 0 | 0
T28 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T29 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T30 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T31 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T32 | [22 empty] | 1 | P3.1G
|  | 7 | 4 | #1/0 ACSR | 255 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1020 | 0 | 0
T33 | [22 empty] | 1 | H1.1G
|  |  | 4 | #1/0 ACSR | 255 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1020 | 0 | 0
T34 | [7 empty] | 1 | P1.3 | [13 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 255 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T35 | [22 empty] | 1 | P3.3G
|  | 40 | 4 | #1/0 ACSR | 255 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T36 | [22 empty] | 1 | P3.3G
. |  |  | 4 | #1/0 ACSR | 200 | 50 | 4 | 1 | C6.52G | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1-PILE |  | SEE NOTE 1. | 800 | 0 | 0
T37 | [7 empty] | 1 | A2.021 | [5 empty] | 120/240V | [5 empty] | 2 | J3.1 | 1 | H1.1G |  | SEE UNIT A6.22G FOR OUTSIDE PHASE
[8 empty] | 1 | A6.22G | [5 empty] | 1-PHASE | [7 empty] | 1 | P3.3G |  | ROUTING.
|  |  | 4 | #1/0 ACSR | 125 | 60 | H2 |  |  | 3 | E1.1La | 3 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 1 | J3.1 | 1 | H1.1G |  | SEE NOTE 1. | 500 | 0 | 75
T38A | [25 empty] | SEE NOTE 3.
SEE NOTE 6.
|  |  | 4 | #1/0 ACSR | 30 | 60 | H2 |  |  | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1G |  | SEE NOTE 1. | 120 | 0 | 0
T38B | [25 empty] | SEE NOTE 3.
|  |  | 4 | #1/0 ACSR | 30 | 60 | H2 |  |  | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1G |  | SEE NOTE 1. | 120 | 0 | 0
T38C | [25 empty] | SEE NOTE 3.
|  |  | 4 | #1/0 ACSR | 30 | 60 | H2 |  |  | 3 | E1.1La | 3 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 1 | J3.1 | 1 | H1.1G |  | SEE NOTE 1. | 120 | 0 | 75
T38D | [25 empty] | SEE NOTE 3.
SEE NOTE 6.
|  |  | 1 | 7#8 | 1200 | 60 | H2 |  |  | 3 | E1.1La | 3 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 1 | J3.1 | 1 | H1.1G |  | SEE NOTE 1. | 1200 | 0 | 75
T39A |  |  |  | ALUMAWELD | [21 empty] | SEE NOTE 3.
SEE NOTE 6.
|  |  | 1 | 7#8 | 1200 | 60 | H2 |  |  | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1G |  | SEE NOTE 1. | 1200 | 0 | 0
T39B |  |  |  | ALUMAWELD | [21 empty] | SEE NOTE 3.
|  |  | 1 | 7#8 | 1200 | 60 | H2 |  |  | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1.1G |  | SEE NOTE 1. | 1200 | 0 | 0
T39C |  |  |  | ALUMAWELD | [21 empty] | SEE NOTE 3.
|  |  | 1 | 7#8 | 1200 | 60 | H2 |  |  | 3 | E1.1La | 3 | F7.0 |  |  | 1 | #4 TRIPLEX |  |  |  | 1 | J3.1 | 1 | H1.1G |  | SEE NOTE 1. | 1200 | 0 | 75
T39D |  |  |  | ALUMAWELD | [21 empty] | SEE NOTE 3.
SEE NOTE 6.
|  |  | 4 | #1/0 ACSR | 125 | 50 | 4 | 1 | C6.52G | 1 | E1.1La | 1 | F7.0 | 1 | G1.4-10 | [5 empty] | 1 | N7.6 | 1 | H1-PILE |  | SEE NOTE 1. | 500 | 0 | 0
T40 | [7 empty] | 1 | A2.021 | [5 empty] | 120/240V | [5 empty] | 2 | J3.1 | 1 | H1.1G |  | SEE UNIT A6.22G FOR OUTSIDE PHASE
[8 empty] | 1 | A6.22G | [5 empty] | 1-PHASE | [7 empty] | 1 | P3.3G |  | ROUTING.
|  |  | 4 | #1/0 ACSR | 100 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 400 | 0 | 0
T41
|  | 26 | 4 | #1/0 ACSR | 255 | 40 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1020 | 0 | 0
T42 | [7 empty] | 1 | P1.3 | [13 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T43 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 265 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1060 | 0 | 0
T44 | [22 empty] | 1 | P3.1G
|  | 5 | 4 | #1/0 ACSR | 265 | 45 | 4 | 1 | C2.21P | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1060 | 0 | 0
T45 | [22 empty] | 1 | P3.3G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T46 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T47 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T48 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T49 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T50 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T51 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T52 | [22 empty] | 1 | P3.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T53 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T54 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T55 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T56 | [22 empty] | 1 | P3.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T57 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T58 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 350 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1400 | 0 | 0
T59 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 175 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 700 | 0 | 0
T60 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T61 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T62 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1100 | 0 | 0
T63 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 1000 | 0 | 0
T64 | [22 empty] | 1 | P3.1G |  | ONE SERVICE.
|  |  | 4 | #1/0 ACSR | 200 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1. | 800 | 0 | 0
T65 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T66 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T67 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 300 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T68 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 280 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T69 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 280 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T70 | [22 empty] | 1 | P3.3G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T71 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T72 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T73 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T74 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T75 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T76 | [22 empty] | 1 | P3.1G
|  | 17 | 4 | #1/0 ACSR | 180 | 40 | 4 | 1 | C6.21 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T77 | [7 empty] | 1 | A1.01 | [13 empty] | 1 | P3.3G
[8 empty] | 2 | A2.021
|  |  | 4 | #1/0 ACSR | 150 | 45 | 3 |  | NOTE 3 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T78A | [22 empty] | 1 | H1.1G |  | SEE NOTE 4.
|  |  | 4 | #1/0 ACSR | 150 | 45 | 3 |  | NOTE 3 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T78B | [22 empty] | 1 | H1.1G |  | SEE NOTE 4.
|  |  | 4 | #1/0 ACSR | 440 | 45 | 3 |  | NOTE 3 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T79A | [22 empty] | 1 | H1.1G |  | SEE NOTE 4.
SEE NOTE 7.
|  |  | 4 | #1/0 ACSR | 440 | 45 | 3 |  | NOTE 3 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T79B | [22 empty] | 1 | H1.1G |  | SEE NOTE 4.
SEE NOTE 7.
|  |  | 4 | #1/0 ACSR | 275 | 40 | 4 | 1 | C6.21 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T80 | [7 empty] | 1 | A1.01 | [13 empty] | 1 | P3.3G
[8 empty] | 2 | A2.021
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T81 | [22 empty] | 1 | P3.1G
|  | 16 | 4 | #1/0 ACSR | 250 | 45 | 4 | 2 | C5.21 | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T82 | [22 empty] | 1 | P3.3G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T83 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T84 | [22 empty] | 1 | P3.1G
[23 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T85 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T86 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C6.91G | 2 | E1.1La | 2 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T87 | [22 empty] | 1 | H1.1G
[23 empty] | 1 | P3.3G
|  |  | 4 | #1/0 ACSR | 250 | 40 | 4 | 1 | C1.11 | [13 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T88 | [22 empty] | 1 | P3.1G
|  |  | 4 | #1/0 ACSR | 250 | 45 | 4 | 1 | C6.21 | 1 | E1.1La | 1 | F7.0 | [9 empty] | 1 | H1-PILE |  | SEE NOTE 1.
T89 | [7 empty] | 1 | A1.01 | [13 empty] | 1 | H1.1G |  | INSTALL #2 ACSR JUMPERS
[8 empty] | 2 | A2.021 | [16 empty] | LAST PILE SUPPORT.
STAKING SHEET NOTES:
1. SEE PROJECT DETAIL DRAWINGS FOR MODIFIED RUS CONSTRUCTION UNITS. UNLESS OTHERWISE INDICATED, GUY LEADS SHALL BE 40 FEET FOR 40 FOOT POLES AND 45 FEET FOR 45 FOOT POLES. SEE SPECIFICATIONS FOR ADDITIONAL REQUIREMENTS.
2. INSTALL NEW POLE IN EXISTING LINE. PLACE TIE-LINE TAP LOWER THAN THE EXSTING MAIN TOGIAK LINE.
3. SEE DETAILS ON DRAWINGS E5.1 AND E5.2 FOR CONSTRUCTION REQUIREMENTS.
4. SEE DETAIL H2.1 FOR CONSTRUCTION REQUIREMENTS.
5. INSTALL 1-1/4" GALVANIZED RIGID CONDUIT WEATHERHEAD AND RISER FOR CONNECTION OF THE PT CONDUCTORS DOWN TO THE RECLOSER CONTROLLER. CONNECT CONDUIT TO THE BOTTOM OF THE
RECLOSER CONTROLLER ENCLOSURE.
6. INSTALL 2" RIGID CONDUIT RISER WITH WEATHERHEAD FOR SERVICE TO THE L-866/L-885 SYSTEM CONTROL PANEL. INSTALL ELECTRICAL SERVICE TO THE CONTROL PANEL EITHER THROUGH THE SIDE OF THE PANEL OR THROUGH THE BACK. DO NOT ENTER THE TOP OF THE PANEL ENCLOSURE. INSTALL WEATHERPROOF HUB AT CONDUIT ENTRANCES TO THE PANEL.
7. INSTALL AERIAL MARKER, TWO PER CONDUCTOR. SPACE MARKERS SUCH THAT MARKERS ARE EVENLY STAGGERED ACCROSS THE RIVER. AERIAL MARKERS SHALL BE 24 IN CHES IN DIAMETER AND SHALL BE CONSTRUCTED OF K-10 ABS. MARKERS BALLS SHALL BE PROVIDED WITH A UV WEATHER CAP AND SHALL BE PROVIDED WITH REFLECTIVE TAPE . PROVIDE ORANGE, YELLOW., AND WHITE MARKER BALLS AND ALTERNATE IN ACCORDANCE WITH FAA AC 70/7460-1L CHG1. SEE SPECIFICATION SECTION 26 53 33, HAZARD WARNING LIGHTING SYSTEMS FOR INSTALLATION REQUIRMENTS.

## Sheet1
Point Number | Raw Description | Style
38 | 1G-1A | POLE P
34 | 1G-2 | EPOLE-P
37 | 1G-3 | POLE P
36 | 1H | EPOLE-P
43 | 1H-1 | EPOLE-P
48 | 1H-1A | POLE P
42 | 1H-2 | EPOLE-P
45 | 1H-2A | POLE P
44 | 1H-2B | POLE P
41 | 1H-3 | EPOLE-P
46 | 1H-3A | POLE P
39 | 1H-4 | EPOLE-P
40 | 1H-4A | POLE P
47 | 1H-4B | POLE P
49 | 1I | EPOLE-P
50 | 1J | EPOLE-P
52 | 1J-1 | EPOLE-P
51 | 1K | EPOLE-P
17 | 2 | EPOLE-P
18 | 2A | EPOLE-P
10 | 2B | EPOLE-P
74 | 2B-1 | EPOLE-P
16 | 2B-2 | EPOLE-P
19 | 2B-2A | POLE P
68 | 2B-2B-1 | POLE P
11 | 2C | EPOLE-P
12 | 2D | EPOLE-P
73 | 2D-1 | POLE P
14 | 2D-2 | POLE P
6 | 2E | EPOLE-P
7 | 2F | EPOLE-P
8 | 2G | EPOLE-P
114 | 2H | EPOLE-P
72 | 2H-1 | POLE P
71 | 2H-2 | POLE P
2 | 2I | EPOLE-P
3 | 2J | EPOLE-P
1 | 2K | EPOLE-P
226 | 2K-1A | POLE P
4 | 2K-1B | POLE P
20 | 3 | EPOLE-P
53 | 4 | EPOLE-P
55 | 5 | EPOLE-P
56 | 6 | EPOLE-P
54 | 7 | EPOLE-P
57 | 8 | EPOLE-P
58 | 9 | EPOLE-P
59 | 10 | EPOLE-P
64 | 11 | EPOLE-P
65 | 12 | EPOLE-P
66 | 15A | POLE P

## Sheet1 (2)
Point Number | Raw Description | Style
5 | 2E-2 | POLE P
70 | 2E-1 | POLE P
77 | 1* | EPOLE-P
23 | 1A | EPOLE-P
76 | 1B | EPOLE-P
75 | 1C | EPOLE-P
24 | 1C-1A | POLE P
25 | 1C-1B | POLE P
26 | 1D | EPOLE-P
28 | 1D-1A | POLE P
27 | 1D-1B | POLE P
29 | 1E | EPOLE-P
30 | 1F | EPOLE-P
31 | 1F-1 | POLE P
32 | 1F-2 | POLE P
33 | 1G | EPOLE-P
35 | 1G-1 | EPOLE-P
38 | 1G-1A | POLE P
34 | 1G-2 | EPOLE-P
37 | 1G-3 | POLE P
36 | 1H | EPOLE-P
43 | 1H-1 | EPOLE-P
48 | 1H-1A | POLE P
42 | 1H-2 | EPOLE-P
45 | 1H-2A | POLE P
44 | 1H-2B | POLE P
41 | 1H-3 | EPOLE-P
46 | 1H-3A | POLE P
39 | 1H-4 | EPOLE-P
40 | 1H-4A | POLE P
47 | 1H-4B | POLE P
49 | 1I | EPOLE-P
50 | 1J | EPOLE-P
52 | 1J-1 | EPOLE-P
51 | 1K | EPOLE-P
17 | 2 | EPOLE-P
18 | 2A | EPOLE-P
10 | 2B | EPOLE-P
74 | 2B-1 | EPOLE-P
16 | 2B-2 | EPOLE-P
19 | 2B-2A | POLE P
68 | 2B-2B-1 | POLE P
11 | 2C | EPOLE-P
12 | 2D | EPOLE-P
73 | 2D-1 | POLE P
14 | 2D-2 | POLE P
6 | 2E | EPOLE-P
7 | 2F | EPOLE-P
8 | 2G | EPOLE-P
114 | 2H | EPOLE-P
72 | 2H-1 | POLE P
71 | 2H-2 | POLE P
2 | 2I | EPOLE-P
3 | 2J | EPOLE-P
1 | 2K | EPOLE-P
226 | 2K-1A | POLE P
4 | 2K-1B | POLE P
20 | 3 | EPOLE-P
53 | 4 | EPOLE-P
55 | 5 | EPOLE-P
56 | 6 | EPOLE-P
54 | 7 | EPOLE-P
57 | 8 | EPOLE-P
58 | 9 | EPOLE-P
59 | 10 | EPOLE-P
64 | 11 | EPOLE-P
65 | 12 | EPOLE-P
66 | 15A | POLE P

## Sheet3
Point Number | Easting | Northing | Raw Description | Style
23 | 1477591.84' | 2178074.23' | 1A | EPOLE-P
76 | 1477497.51' | 2178138.62' | 1B | EPOLE-P
75 | 1477454.21' | 2178168.30' | 1C | EPOLE-P
24 | 1477559.44' | 2178220.60' | 1C-1A | POLE P
25 | 1477487.58' | 2178279.34' | 1C-1B | POLE P
26 | 1477343.52' | 2178167.36' | 1D | EPOLE-P
28 | 1477397.78' | 2178084.36' | 1D-1A | POLE P
27 | 1477320.78' | 2178264.26' | 1D-1B | POLE P
29 | 1477199.06' | 2178148.43' | 1E | EPOLE-P
30 | 1477051.55' | 2178129.10' | 1F | EPOLE-P
31 | 1477069.40' | 2177995.83' | 1F-1 | POLE P
32 | 1477041.33' | 2177901.19' | 1F-2 | POLE P
33 | 1476969.53' | 2178118.35' | 1G | EPOLE-P
35 | 1476968.04' | 2178267.00' | 1G-1 | EPOLE-P
38 | 1477085.84' | 2178264.80' | 1G-1A | POLE P
34 | 1476966.12' | 2178459.82' | 1G-2 | EPOLE-P
37 | 1477050.15' | 2178456.24' | 1G-3 | POLE P
36 | 1476805.73' | 2178096.90' | 1H | EPOLE-P
43 | 1476773.58' | 2178221.12' | 1H-1 | EPOLE-P
48 | 1476816.52' | 2178005.99' | 1H-1A | POLE P
42 | 1476751.81' | 2178305.13' | 1H-2 | EPOLE-P
45 | 1476639.60' | 2178252.06' | 1H-2A | POLE P
44 | 1476516.73' | 2178192.44' | 1H-2B | POLE P
41 | 1476737.09' | 2178360.17' | 1H-3 | EPOLE-P
46 | 1476808.72' | 2178401.30' | 1H-3A | POLE P
39 | 1476703.40' | 2178492.14' | 1H-4 | EPOLE-P
40 | 1476571.76' | 2178434.60' | 1H-4A | POLE P
47 | 1476816.07' | 2178541.58' | 1H-4B | POLE P
49 | 1476625.29' | 2178073.24' | 1I | EPOLE-P
50 | 1476457.30' | 2178051.22' | 1J | EPOLE-P
52 | 1476477.46' | 2177974.63' | 1J-1 | EPOLE-P
51 | 1476306.67' | 2178031.54' | 1K | EPOLE-P
77 | 1477789.11' | 2178012.76' | 1* | EPOLE-P
17 | 1477937.18' | 2177992.64' | 2 | EPOLE-P
18 | 1477925.39' | 2178135.60' | 2A | EPOLE-P
10 | 1477913.70' | 2178278.69' | 2B | EPOLE-P
74 | 1477810.16' | 2178292.44' | 2B-1 | EPOLE-P
16 | 1477706.62' | 2178306.19' | 2B-2 | EPOLE-P
19 | 1477615.73' | 2178362.46' | 2B-2A | POLE P
68 | 1477696.29' | 2178450.58' | 2B-2B-1 | POLE P
11 | 1477993.42' | 2178541.89' | 2C | EPOLE-P
12 | 1478073.13' | 2178805.08' | 2D | EPOLE-P
73 | 1477929.36' | 2178827.80' | 2D-1 | POLE P
14 | 1477785.63' | 2178850.56' | 2D-2 | POLE P
6 | 1478152.84' | 2179068.27' | 2E | EPOLE-P
5 | 1477909.20' | 2179077.57' | 2E-2 | POLE P
70 | 1478031.02' | 2179072.92' | 2E-1 | POLE P
7 | 1478204.02' | 2179237.24' | 2F | EPOLE-P
8 | 1478090.58' | 2179431.55' | 2G | EPOLE-P
114 | 1477976.82' | 2179626.42' | 2H | EPOLE-P
72 | 1477864.79' | 2179644.36' | 2H-1 | POLE P
71 | 1477752.44' | 2179662.85' | 2H-2 | POLE P
2 | 1477863.06' | 2179821.28' | 2I | EPOLE-P
3 | 1477700.64' | 2179973.28' | 2J | EPOLE-P
1 | 1477545.15' | 2180118.79' | 2K | EPOLE-P
226 | 1477459.43' | 2180088.12' | 2K-1A | POLE P
4 | 1477667.53' | 2180257.47' | 2K-1B | POLE P
20 | 1478137.14' | 2177920.01' | 3 | EPOLE-P
53 | 1478920.41' | 2177338.55' | 4 | EPOLE-P
55 | 1479100.85' | 2177268.55' | 5 | EPOLE-P
56 | 1479285.95' | 2177196.72' | 6 | EPOLE-P
54 | 1479443.16' | 2177135.76' | 7 | EPOLE-P
57 | 1479557.47' | 2177048.78' | 8 | EPOLE-P
58 | 1479651.29' | 2176910.61' | 9 | EPOLE-P
59 | 1479755.73' | 2176740.63' | 10 | EPOLE-P
64 | 1479883.80' | 2176613.43' | 11 | EPOLE-P
65 | 1480008.75' | 2176600.33' | 12 | EPOLE-P
66 | 1480715.14' | 2176545.77' | 15A | POLE P