## STAKSHT
GRAY STASSEL ENGINEERING, INC. | [11 empty] | PORT HEIDEN DISTRIBUTION
P.O. BOX 111405 | [11 empty] | UPGRADE PROJECT
ANCHORAGE, ALASKA 99511 | [11 empty] | PORT HEIDEN, ALASKA
(907) 349-0100
REV. NO. | DATE |  |  | BY |  | DESCRIPTION | [11 empty] | DESIGNER | DATE
2 | 2022-03-14 |  |  | CWV |  | ISSUED FOR CONSTRUCTION. | [10 empty] | CWV |  | 2022-03-14
| PRIMARY | [8 empty] | SECONDARY CONDUCTOR |  |  | SECONDARY |  | MISCELLANEOUS
LOCATION | CONDUCTOR |  |  | PRIMARY |  |  |  | SERVICE |  |  | BACKFEED |  | SERVICE |  | CONSTRUCTION |  | REMARKS, COMMENTS, NOTES
NUMBER |  |  | Back | ASSEMBLY |  | XFMRS |  |  |  | Back |  |  | UNITS |  | UNITS
| No. | SIZE/TYPE | Span | No. | Units | No. | Units | No. | SIZE/TYPE | Span | No. | SIZE/TYPE | No. | Units | No. | Units
PHASE 1
SC2 | [14 empty] | 1 | UM6.C2 | REMOVE ONE UM6.EL2 ELBOW AND TURN OVER TO UTILITY.
(EXISTING) | [16 empty] | SEE PLAN DRAWINGS FOR REMOVAL OF TRANSFORMER.
JB2W |  |  |  | 3 | UM6.EL2 | [11 empty] | REMOVE THREE UM6.C2 CAPS AND TURN OVER TO UTILITY.
(EXISTING) | [16 empty] | SEE NOTE 6.
SC-AN-1 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE PLAN DRAWINGS FOR ADDITIONAL DETAILS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 3 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.JN2222
SC-AN-2 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 8 | UM6.C2 | SEE NOTE 6.
|  |  |  | 7 | UM6.EL2
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-AN-2 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-25 | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 3 | UJ2.4 | 1 | UH1.1 | STREET LIGHT CONNECTION.
|  |  |  | 1 | UM6.EL2 | [9 empty] | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
PED-AN-2A | [7 empty] | 1 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | TWO SINGLE-PHASE SERVICES.
[8 empty] | 1 | #1/0 TRIPLEX | NOTE 2 |  |  | 1 | UJ3.1 |  |  | SEE NOTE 8.
[13 empty] | 2 | UQ1.1B1a
PED-AN-2B | [7 empty] | 2 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | TWO SINGLE-PHASE SERVICES.
[13 empty] | 1 | UJ3.1 |  |  | SEE NOTE 8.
[13 empty] | 2 | UQ1.1B1a
SC-AN-3 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-AN-4 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-AN-5 |  | NOT USED
SC-AN-6 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 10 | UM6.EL2 | [9 empty] | 5 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-AN-6 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-25 | 2 | #1/0 TRIPLEX | NOTE 2 |  |  | 3 | UJ2.4 | 1 | UH1.1 | TWO SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 |  |  | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 2 | UQ1.1B1a | 2 | UM6.C2 | STREET LIGHT CONNECTION.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
PED-AN-6A | [7 empty] | 1 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | ONE SINGLE-PHASE SERVICE.
[13 empty] | 1 | UQ1.1B1a |  |  | SEE NOTE 8.
SC3 | 3 | #1/0 JCN | NOTE 2 | 3 | UM6.EL2 | [11 empty] | EXISTING SECTIONALIZING CABINET.
EXISTING | [16 empty] | REMOVE THREE UM6.C2 AND TURN OVER TO THE UTILITY.
SEE NOTE 6.
SC-P-1 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 8 | UM6.EL2 | [9 empty] | 7 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-P-1A | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX |  |  |  | 3 | UJ2.4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
TR-P-1B | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX |  |  |  | 3 | UJ2.4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 |  |  | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 1 | UQ1.1B1a | 2 | UM6.C2 | STREET LIGHT CONNECTION.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
SC-P-2 |  | NOT USED
SC-P-3 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-P-4 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 7 | UM6.EL2 | [9 empty] | 8 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-P-4 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 2 | #2 TRIPLEX |  |  |  | 3 | UJ2.4 | 1 | UH1.1 | TWO SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 2 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
SC-P-5 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 7 | UM6.EL2 | [9 empty] | 8 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-P-5 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 3 | UJ2.4 | 1 | UH1.1 | STREET LIGHT CONNECTION.
|  |  |  | 1 | UM6.EL2 | [9 empty] | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
PED-P-5A | [7 empty] | 2 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | TWO SINGLE-PHASE SERVICES.
[13 empty] | 2 | UQ1.1B1a |  |  | SEE NOTE 8.
[13 empty] | 1 | UJ3.1
SC-P-6 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-P-7 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 8 | UM6.EL2 | [9 empty] | 7 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-P-7A | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 4 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2.6 | 1 | UH1.1 | FOUR SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 4 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
PED-P-7A | [7 empty] | 1 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | ONE SINGLE-PHASE SERVICE.
[8 empty] | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 1 | UQ1.1B1a |  |  | STREET LIGHT CONNECTION.
[13 empty] | 1 | UJ3.1 |  |  | SEE NOTE 8.
TR-P-7B | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 3 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2.6 | 1 | UH1.1 | THREE SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 3 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
PED-P-7B | [7 empty] | 1 | #8 DUPLEX CU | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | STREET LIGHT CONNECTION.
[13 empty] | 1 | UJ3.1 |  |  | SEE NOTE 8.
SC-P-8 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 6 | UM6.EL2 | [9 empty] | 9 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-P-9 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 4 | UM6.EL2 | [9 empty] | 11 | UM6.C2 | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-P-9 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 3 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2.6 | 1 | UH1.1 | THREE SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 3 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
PED-P-9 | [7 empty] | 1 | #2 TRIPLEX | NOTE 2 | 1 | #2/0 TRIPLEX | 3 | UJ4.1 |  |  | ONE SINGLE-PHASE SERVICE.
[8 empty] | 1 | #8 DUPLEX CU | NOTE 2 |  |  | 1 | UQ1.1B1a |  |  | STREET LIGHT CONNECTION.
[13 empty] | 1 | UJ3.1 |  |  | SEE NOTE 8.
SC7 |  |  |  | 2 | UM6.EL2 | [11 empty] | REMOVE ONE UM6.C2 AND TURN OVER TO UTILITY.
EXISTING | [16 empty] | SEE NOTE 6.
SC-H-4 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [9 empty] | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
|  |  |  | 1 | UM6.JN2222
SC-H-5 | 1 | #2 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 1 | UH1.1 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [9 empty] | 2 | UM6.C2 | SINGLE PHASE SECTIONALIZING CABINET.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
TR-H-8B | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2.6 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 3 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
|  |  |  | 1 | UM6.JN2222
PHASE 2
SC3 | [16 empty] | SECTIONALIZING CABINET TO BE REMOVED IN ITS ENTIRETY.
EXISTING | [16 empty] | SEE PLAN SHEET.
SC-AN-6 |  |  |  | 3 | UM6.EL2 | [11 empty] | SEE NOTE 6.
(PHASE 1) | [16 empty] | EXISTING SECTIONALIZING CABINET INSTALLED UNDER PHASE 1.
SC-DOT-1 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 8 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 7 | UM6.EL2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-DOT-2 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 2 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [11 empty] | SINGLE PHASE SECTIONALIZING CABINET.
|  |  |  | 2 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
TR-DOT-2 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-25 | [5 empty] | 3 | UJ2-4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | CONNECT TRANSFORMER TO EXISTING SECONDARY CONDUCTORS. SEE
|  |  |  | 1 | UM6.PK2 | [11 empty] | PLAN SHEETS. OPERATE DME ON GENERATOR DURING TRANSFORMER
REPLACEMENT. COORDINATE WITH FAA.
SC-DOT-3 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 6 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 9 | UM6.EL2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
SC-DOT-4 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 8 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 7 | UM6.EL2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-DOT-4 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
SC-DOT-5 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 2 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [11 empty] | SINGLE-PHASE SECTIONALIZING CABINET.
|  |  |  | 2 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
SC-DOT-6 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 2 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [11 empty] | SINGLE-PHASE SECTIONALIZING CABINET.
|  |  |  | 2 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
TR-DOT-6 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | SEE PLAN SHEET FOR SERVICE CONNECTION REQUIREMENTS.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
SC-DOT-7 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 6 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 9 | UM6.EL2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-DOT-7 | 2 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-25 | 2 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | TWO SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 2 | UQ1.1B1a | 1 | UM6.C2 | TRANSFORMER IS PROVIDED WITH 12.47 KV DELTA PRIMARY CONNECTION.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
SC-DOT-8 | 3 | #1/0 JCN | NOTE 2 | 1 | 15US3.PJ.2222a | [9 empty] | 8 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 7 | UM6.EL2 | [11 empty] | SEE NOTE 6.
|  |  |  | 3 | UM6.PK2
|  |  |  | 3 | UM6.JN2222
TR-DOT-8 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 2 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | TWO SINGLE-PHASE SERVICES.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 2 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
SC-DOT-9 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 2 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [11 empty] | SINGLE-PHASE SECTIONALIZING CABINET.
|  |  |  | 2 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
TR-DOT-9 | 1 | #1/0 JCN | NOTE 2 | 1 | UM1-7NC | 1 | UG1.3-15 | 1 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | SEE PLAN SHEET FOR SERVICE CONNECTION REQUIREMENTS.
|  |  |  | 1 | UM6.PK2 | [11 empty] | SEE NOTE 6.
SC-DOT-10 | 1 | #1/0 JCN | NOTE 2 | 1 | 15US1.PJ.2222a | [9 empty] | 2 | UM6.C2 | SEE DETAIL ON PLAN SHEETS.
|  |  |  | 2 | UM6.EL2 | [11 empty] | SINGLE-PHASE SECTIONALIZING CABINET.
|  |  |  | 2 | UM6.PK2 | [11 empty] | SEE NOTE 6.
|  |  |  | 1 | UM6.JN2222
TR-DOT-10 | 1 | #1/0 JCN | NOTE 2 | 1 | UF1.BNa | 1 | UG1.3-15 | 1 | #2 TRIPLEX | NOTE 2 |  |  | 3 | UJ2-4 | 1 | UH1.1 | ONE SINGLE-PHASE SERVICE.
|  |  |  | 1 | UM6.EL2 | [7 empty] | 1 | UQ1.1B1a | 2 | UM6.C2 | SEE NOTE 6.
|  |  |  | 1 | UM6.PK2
STAKING SHEET NOTES:
1. REFER TO THE DRAWINGS FOR PHYSICAL LAYOUT OF SYSTEM AND FOR ADDITIONAL NOTES OR ADDITIONA LINFORMATION. DETAILS OF DEMOLITION MAY NOT BE INCLUDED IN THE STAKING SHEETS. SEE PLAN SHEETS FOR ALL REQUIRED CONSTRUCTION ACTIVITIES AND COORDINATION.
2. SEE PLAN SHEETS FOR BACKSPAN DISTANCE.
3. RUS UNIT UJ3.1 SHALL BE A SINGLE-PHASE SECONDARY PEDESTAL WITHOUT A STAKE. SEE SPECIFICATIONS.
4. ALL TRANSFORMERS SHALL HAVE GROUND SLEEVES. SEE SPECIFICATIONS.
5. DUPLEX - DUPLEX UD CONDUCTOR. SEE SPECIFICATIONS.
TRIPLEX - TRIPLEX UD CONDUCTOR. SEE SPECIFICATIONS.
6. SELECT WIRE SIZE FOR UM6.EL2 BASED ON WIRE SIZE INDICATED.
7. RUS UNITS UJ2.4, UJ2.6, AND UJ4.1 SHALL BE INSULATED. SEE SPECIFICATIONS.
8. UJ4.1 ARE SECONDARY INSULATED CONNECTOR BLOCKS.